Rm of Whitemouth

Public Water System

Annual Report

2025

Name of the Public Water System: Whitemouth Rural Pipeline

Name of the Legal Owner: RM of Whitemouth

Contact Person: Lacey Smith (COA)

Phone: (204) 348-2221

Fax: (204) 348-2576

Email: cao@rmwhitemouth.com

Website: www.rmwhitemouth.com

Name of Operators: Glen Campbell, Sr. Utility Operator – Water Treatment 2,

Water Distribution 1, Waste Water Small System

Matthew Pommer, Operator in Training

- Water Treatment OIT, Water Distribution OIT

Phone during business hours: (204) 348-2574 or (204) 348-2221

Date prepared: March 27/26	 	 	 	 	 Prepared By: Glen Campbell

Table of Contents

Introduction..........................................................................................................

- Description of the Water System ........................................................................

  - Water Supply Source ...........................................................................................

  - Water Treatment Processes .................................................................................

  - Water Treatment and Distribution Capacities .....................................................

  - Distribution System ..............................................................................................

  - Number of Connections and Water User Types ...................................................

  - System Classification and Certification ................................................................

- Disinfection System in Use ...................................................................................

  - Type of Disinfection System Used ........................................................................

  - Redundancy and Monitoring ................................................................................

  - Disinfectant Residual Overall Performance and Results ......................................

- List of Water Quality Standards ...........................................................................

  - Disinfection Monitoring and Reporting ................................................................

  - Lead Testing Monitoring and Reporting ……………………………………………………………

  - Bacteriological Monitoring and Reporting ...........................................................

  - Turbidity Monitoring and Reporting ....................................................................

  - Disinfection By-products Monitoring and Reporting ...........................................

  - Manganese Monitoring and Reporting ……………………………………………………………

  - Total Microcystins Monitoring and Reporting………………………………………………….

- Water System Incidents and Corrective Actions ..................................................

  - Water Breaks ........................................................................................................

  - Water Hook-Ups ...................................................................................................

4.3 Other Incidents or Corrective Actions ……………………………………………………………….

- Drinking Water Safety Orders and Corrective Actions .........................................

- Boil Water Advisories and Corrective Actions ......................................................

- Warnings Issued or Charges Laid .........................................................................

- Major Expenses Incurred .....................................................................................

- Anticipated Future Costs, Expansion and/or Increased Production ....................

10. Certificate of Analysis for General Chemistry 2025 - separate attachment available at the RM Office or on website

Introduction:

The 2025 Public Water System Annual Report summarizes the ability of the RM of Whitemouth to produce and provide safe potable water to our constituents which meets provincial regulations.

- Description of the Water System:

The RM of Whitemouth Public Water System provides potable drinking water to a population of approximately 1500 residents. Treated water from the water treatment plant met all health as stated in the Guidelines for Canadian Drinking Water Quality as well as provincial regulations. Aesthetic objectives in the Guidelines for Canadian Drinking Water Quality met all.

1.1 Water Supply Source

The RM of Whitemouth Water Treatment Plant draws its supply water from Natalie Lake of the Winnipeg River. The Winnipeg River has an abundant supply of high-quality water which is easily treated to meet all standards.

The Water Treatment Plant intake is approximately 12 feet below the surface of the river. The water is then pumped into the Water Treatment Plant situated in Seven Sisters Falls, Mb on Waterline Road.

1.2 Water Treatment Processes

The high quality of water which comes out of the Winnipeg River requires a minimal amount of treatment to meet all provincial requirements. Upon entering the water treatment plant and entering our Actiflo treatment system the raw water is injected with a product called Hydrex 3613 Polymere, which is a flocculating agent, and Aluminum Sulphate Solution, which is a further flocculating agent, and Actisand, which is fine silica sand. These processes are geared mainly towards treating the turbidity and colour of the raw water. The raw water comes out of the Winnipeg River with an average turbidity between 2-10 nephelometric turbidity units (NTU). The Actiflo processes drop this figure to on average between 0.4 -1.0 NTU.  The water which has been treated through the Actiflo. After going through the filter, the treated water is at approximately 0.030-0.070 NTU. This number is approximately 11% of our regulated limit. The legal requirement for our treated water is 0.3 NTU after the filter. The water is then stored in a 873,000 litre reservoir.

A result of the Actiflo/ Chemical processes is that the water pH drops to approximately 6.2-6.5. This water is then treated with Sodium Hydroxide 25% solution to raise the pH from 6.2-6.5 to a level of 7.6-7.8. This means that the treated water is very close to neutral which aids in controlling corrosion and deposits. The reservoir water is further treated with Sodium Hyprochlorite 12% as a disinfecting agent. Our distribution water must leave the water treatment plant with a minimum of 0.5mg per litre of free chlorine residual and have a minimum of 0.1 mg per litre in all areas of the distribution.

1.3 Water Treatment and Distribution Capacities

The RM of Whitemouth Water Treatment Plant operates at an incoming rate of 15 litres per second and runs for approximately 8 - 12 hours per day using two 20hp distribution duty pumps. We treat approximately 465,000 litres daily on average.   Distribution system pressure is maintained at between 55-60psi using frequency drive pumps and a pressure relief system.

1.4 Distribution System

RM of Whitemouth’s water distribution system is approximately 125 kilometres long and is comprised of approximately 50% PVC and 50% HDPE. Distribution piping varies in size from 8” to 2”.

1.5 Number of Connections, and water user types

RM of Whitemouth has approximately 525 connections with a large different type of users from residential, commercial, and farms. From small users to large users. From year round to seasonal connections. In 2019 the RM of Whitemouth started selling water to the RM of Lac Du Bonnet Brookfield Utility / Awanipark in the LGD of Pinawa which added another 150 connections. For a total of 675 connections.

1.6 System Classification and Certification under the Water and Wastewater Facility Operators Regulation under the Environment Act.

A Class 2 Water Treatment Facility

A Class 1 Water Distribution System

A Small Systems Waste Water

Note: The Sr. Utility Operator (Operator in charge) meets all certifications for Water Treatment and Water Distribution and Waste Water

- Disinfection System in Use.

The RM of Whitemouth uses Sodium Hypochlorite 12% as our disinfection method. Disinfection is the selective destruction or inactivation of potential disease-causing organisms in water. As per the Drinking Water Safety Act the RM of Whitemouth Public Water System must ensure that we maintain a free disinfectant residual of at least:

    - 0.5 mg of free chlorine per litre of water is detectable at the point where water enters the distribution system, after a minimum contact time of 20 minutes

    - O.1 mg of free chlorine per litre of water is detectable at all times at any point in the distribution network.

  - Type of Disinfection System Used

The RM of Whitemouth Water Treatment Plant disinfects using Sodium Hypochlorite 12% concentration. Chlorine is added to the system using 2 peristaltic pumps, one as primary one as backup should one fail or fault the other will automatically switch.

  - Need for Redundancy and Monitoring

The “Drinking Water and Safety Act” requires that disinfection is continuously maintained. To ensure this we use two separate chlorine pumps allowing for redundancy in the system itself where one side can be turned off and the disinfecting needs will be met by the remaining side and some spare parts which are more prone to fail or need replacing.

Disinfectant total and free residuals are checked and recorded daily at the water treatment plant and bi-weekly at points throughout the distribution system. Results are recorded on the appropriate monitoring forms and are sent to the regional Drinking Water Officer at the end of each month.  SCADA system that records free chlorine levels on a continuous basis.

  - Disinfectant Residual Overall Performance and Results

For the year 2025 the RM of Whitemouth Public Water System has met 100% of the regulatory requirements for treated water and 100% for distributed water.

- List of Water Quality Standards

The Province of Manitoba has adopted a number of water quality standards from the Guidelines for Canadian Drinking Water Quality, developed by Health Canada. The parameters are health-based and they express the maximum acceptable concentrations for drinking water. Concentration values in excess of the standards constitute a possible health related issue and require corrective actions. The 2025 results for the RM of Whitemouth Public Water System are summarized in the following tables:

  - Disinfection Monitoring and Reporting

|  | Regulatory Requirement | Water System Performance |
| --- | --- | --- |
| Free Chlorine Residual entering the Distribution System | >0.5 mg/L | Meets requirements |
| Frequency of Testing | Daily | Meets requirements |
| Free Chlorine Residual in the Distribution System | >0.1 mg/L | Meets requirements |
| Frequency of Testing | Bi-Weekly | Meets requirements |
| Report Submissions | Monthly | Meets requirements |

| Month | Free Average mg/L | Total Average mg/L |
| --- | --- | --- |
| January | 1.244 | 1.50 |
| February | 1.225 | 1.49 |
| March | 1.236 | 1.49 |
| April | 1.264 | 1.51 |
| May | 1.274 | 1.49 |
| June | 1.204 | 1.44 |
| July | 1.252 | 1.52 |
| August | 1.228 | 1.50 |
| September | 1.214 | 1.47 |
| October | 1.264 | 1.53 |
| November | 1.261 | 1.53 |
| December | 1.245 | 1.49 |

  - Lead Testing Monitoring and Reporting

|  | Regulatory Requirement | Water System Performance |
| --- | --- | --- |
| Number of Completed tests 20 per year | 20 | Meets Requirements |
| Number of samples Pass Below 0.005mg/l | 20 of 20 | Meets Requirements |

Lead testing Results

| RDT | 30MS - 1 of 2 | 30MS - 2 of 2 |
| --- | --- | --- |
| Result (mg/L) | Result (mg/L) | Result (mg/L) |
| 0.00161 |  |  |
| 0.00244 |  |  |
| 0.00149 |  |  |
| 0.00109 |  |  |
| 0.00052 |  |  |
| 0.0005 |  |  |
| 0.000249 |  |  |
| 0.00183 |  |  |
| 0.000116 |  |  |
| 0.000145 |  |  |
| 0.000015 |  |  |
| 0.000013 |  |  |
| 0.000139 |  |  |
| 0.000171 |  |  |
| 0.000152 |  |  |
| 0.000642 |  |  |
| 0.0003 |  |  |
| 0.000202 |  |  |
| 0.000163 |  |  |
| 0.000363 |  |  |

  - Bacteriological Monitoring and Reporting

|  | Regulatory Requirement | Water System Performance |
| --- | --- | --- |
| Number of Raw/Incoming Water Samples | Bi-weekly | Meets requirements |
| Number of Treated Water Samples | Bi-weekly | Meets requirements |
| Number of Distribution Water Samples | 78 | Meets requirements |
| Frequency of Testing | Bi-weekly | Meets requirements |
| Total Coliform (TC) Present in Water Samples | 0 TC per 100mL | Meets requirements |
| E. Coli (EC) Present in Water Samples | 0 EC per 100mL | Meets requirements |

  - Turbidity Monitoring and Reporting

|  | Regulatory Requirement | Water System Performance |
| --- | --- | --- |
| Chemically assisted, rapid gravity filtration process | <0.3NTU in at Least 95% Of samples | Meets requirements |
| Standard | Never to exceed 1.0 NTU | Meets requirements |
| Frequency of Testing | Continuous | Meets requirements |
| Report Submissions | Monthly (An effective treatment barrier through monitoring / reporting) | Meets requirements |

| Month | Raw Average NTU | Treated Average NTU |
| --- | --- | --- |
| January | 2.11 | 0.045 |
| February | 1.95 | 0.044 |
| March | 2.07 | 0.046 |
| April | 2.02 | 0.047 |
| May | 3.56 | 0.047 |
| June | 5.03 | 0.065 |
| July | 5.09 | 0.064 |
| August | 4.57 | 0.054 |
| September | 5.11 | 0.049 |
| October | 4.46 | 0.041 |
| November | 2.96 | 0.041 |
| December | 1.69 | 0.041 |

  - Disinfection By-products Monitoring and Reporting

  - Manganese Monitoring and Reporting

|  | Regulatory Requirement | Water System Performance |
| --- | --- | --- |
| Manganese Sample Requirements | Yearly | Testing done Yearly During General Chemistry |
| Manganese Standards | <0.12 mg/L | Meets Requirements 0.00054mg/l results |

|  | Regulatory Requirement | Water System Performance |
| --- | --- | --- |
| Trihalomethane sampling requirements | Quarterly | Testing required every 2nd year Completed 2025 |
| Total Trihalomethane Standard | <0.1mg/L | Passed 0.0759 mg/l 2025 results |
| Haoacetic Acid sampling requirements | Quarterly | Testing required every 2nd year Completed in 2025 |
| Haloacetic Acid Standard | <0.08mg/L | Passed 0.0449 mg/l 2025 results |

  - Total Microcystins Monitoring and Reporting

|  | Regulatory Requirements | Water System Performance |
| --- | --- | --- |
| Microcystins Sample Requirements | Yearly | Testing done Yearly in August |
| Microcystins Standards | <0.0015 mg/l | Meets Requirements <0.0002 mg/l Results |

- Water System Alterations, Incidents and Corrective Actions

  - Water Breaks

Most waterline repairs were done while the waterline was still under minimal positive pressure to ensure no in line contamination. After repairs were completed, waterlines were flushed and checked to make sure that a satisfactory disinfectant residual was maintained prior to being put back into service. Most repairs were done in such a way as to minimize down time for users and as much advance notice given as possible. The RM of Whitemouth had 5 repairs in 2025.

  - Water Hook-Ups                                                                                                        During 2025 the RM had 7 new water hookups.

4.3 Other Incidents or Corrective Actions                                                                                During 2025 the RM of Whitemouth Public Water System had no incidents or corrective actions required

- Drinking Water Safety Orders on Water System and Corrective Actions Taken    During 2025, there were no Drinking Water Safety Orders issued for the RM of Whitemouth Public Water System.

- Boil Water Advisories Issued on Water System and Corrective Actions Taken During 2025 the RM of Whitemouth Public Water System did have 1 Boil Water Advisories.  Due to depressurization of distribution system in the Town of Whitemouth, due to equipment failure our distribution pumps failed to continue to run causing the line to depressurize. BWA issued November 20 and rescinded November 24, 2025

- Warnings Issued or Charges Laid on Water System in Accordance with The Drinking Water Safety Act

During 2025 the RM of Whitemouth Public Water System did not have any warnings or charges

- Major Expenses Incurred in 2025                                                                               In 2025 The RM of Whitemouth continued installing curb stops to residents that did not have. 8 new curb stops were installed. Due to age and cost of maintaining caustic chemical pumps at the treatment plant, 2 new pumps were ordered and installed. 3 new turbidity meters at the treatment plant were ordered and installed due to age and repair parts being discontinued. Every 7 years our utility has to have an Engineered Assessment done as per our license and in 2025 that was completed.

- Anticipated Future Major Cost Items, System Expansion and/or Increased or Decreased Production                                                                                                 We will continue to budget for adding so many new curb stops for those that do not have. Budgeting for 3 upgraded PH/Chlorine analyzers. Due to parts being discontinued new sensors and rebuild kits are required. As per our license we are required to have these working as they record our Chlorine and PH 24 per day. 2 new alum chemical pumps are required due to age and repair parts availability. These pumps are original pumps that will be replaced. A new Cla-val globe valve is required for the truck fill at the water treatment plant to solve issues. This valve is an original valve.