|  |  | CERTIFICATE OF ANALYSIS (GUIDELINE EVALUATION) |  |  |
| --- | --- | --- | --- | --- |
| Work Order Client Contact Address Telephone Project PO C-O-C number Sampler Site Quote number No. of samples received No. of samples analysed | : : : : : : : : : : : : : | WP2514871 Manitoba Conservation & Climate Amrith Kumar Box 4000, #4 Highway 502 Lac du Bonnet Manitoba Canada R0E 1A0 204 340 3423 Whitemouth - PWS - 249.25 ---- ---- ---- Whitemouth - PWS 249.25 2025 WTP Chemistry 2 2 | Laboratory Account Manager Address Telephone Date Samples Received Date Analysis Commenced Issue Date | : ALS Environmental - Winnipeg : Sheriza Rajack-Ahamed : 1329 Niakwa Road East, Unit 12 Winnipeg MB Canada R2J 3T4 : +1 204 255 9720 : 02-Sep-2025 14:44 : 02-Sep-2025 : 11-Sep-2025 08:52 |

This report supersedes any previous report(s) with this reference. Results apply to the sample(s) as submitted. This document shall not be reproduced, except in full.

This Certificate of Analysis contains the following information:

General Comments

Analytical Results

Additional information pertinent to this report will be found in the following separate attachments: Quality Control Report, QC Interpretive report to assist with Quality Review and Sample

Receipt Notification (SRN).

Guideline Comparison

# Signatories

This document has been electronically signed by the authorized signatories below.  Electronic signing is conducted in accordance with US FDA 21 CFR Part 11.

Signatories	Position	Laboratory Department

| Kevin Baxter | Metals, Winnipeg, Manitoba |
| --- | --- |
| Kevin Baxter | Inorganics, Winnipeg, Manitoba |
| Kevin Baxter | Administration, Winnipeg, Manitoba |
| Lee McTavish | Inorganics, Winnipeg, Manitoba |

## Summary of Guideline Breaches by Sample

| SampleID/Client ID | Matrix | Analyte | Analyte Summary | Guideline | Category | Result | Limit |
| --- | --- | --- | --- | --- | --- | --- | --- |
| RM of Whitemouth Rural Pipeline 1 - Raw Raw | Water | Colour, true | May interfere with disinfection; removal is important to ensure effective treatment. | CDWG | AO | 20.1 CU | 15 CU |
|  | Water | Turbidity | For systems that use groundwater, turbidity should generally be below 1.0 NTU. Filtration systems should be designed and operated to reduce turbidity levels as low as reasonably achievable and strive to achieve a treated water turbidity target from individual filters of less than 0.1 NTU. | CDWG | AO | 3.83 NTU | 1 NTU |
|  | Water | Iron, total | Based on taste and staining of laundry and plumbing fixtures; no evidence exists of dietary iron toxicity in the general population. | CDWG | AO | 130 µg/L | 100 µg/L |
|  | Water | Aluminum, total | The OG value is established to minimize the potential for the distribution system and to avoid other operational and aesthetic issues. It takes treatment achievability into consideration. | CDWG | OG | 119 µg/L | 100 µg/L |
| RM of Whitemouth Rural Pipeline 2 - Treated Treated | Water | Aluminum, total | The OG value is established to minimize the potential for the distribution system and to avoid other operational and aesthetic issues. It takes treatment achievability into consideration. | CDWG | OG | 164 µg/L | 100 µg/L |

## General Comments

The analytical methods used by ALS are developed using internationally recognized reference methods (where available), such as those published by US EPA, APHA Standard Methods, ASTM, ISO, Environment Canada, BC MOE, and Ontario MOE.  Refer to the ALS Quality Control Interpretive report (QCI) for applicable references and methodology summaries. Reference methods may incorporate modifications to improve performance.

Where a reported less than (<) result is higher than the LOR, this may be due to primary sample extract/digestate dilution and/or insufficient sample for analysis.

Where the LOR of a reported result differs from standard LOR, this may be due to high moisture content, insufficient sample (reduced weight employed) or matrix interference.

When sampling time information is not provided by the client, sampling dates are shown without a time component.  In these instances, the time component has been assumed by the laboratory for processing purposes.

Application of guidelines is provided "as is" without warranty of any kind, either expressed or implied, including, but not limited to fitness for a particular purpose, or non-infringement. ALS assumes no responsibility for errors or omissions in the information. Guidelines are not adjusted for the hardness, pH or temperature of the sample (the most conservative values are used).  Measurement uncertainty is not applied to test results prior to comparison with specified criteria values.

Key:	LOR: Limit of Reporting (detection limit).

Unit	Description

| - | no units |
| --- | --- |
| % | percent |
| % T/cm | % transmittance per centimetre |
| AU/cm | absorbance units per centimetre |
| CU | colour units (1 cu = 1 mg/l pt) |
| meq/L | milliequivalents per litre |
| mg/L | milligrams per litre |
| NTU | nephelometric turbidity units |
| pH units | pH units |
| µg/L | micrograms per litre |
| µS/cm | microsiemens per centimetre |

>: greater than. <: less than.

Red	shading is applied where the result or the LOR is greater than the Guideline Upper Limit (or lower than the Guideline Lower Limit, if applicable).

For drinking water samples, Red shading is applied where the result for E.coli, fecal or total coliforms is greater than or equal to the Guideline Upper Limit.

## Analytical Results Evaluation